**Weott CSD’s Operator’s Report**

**5-28-2025**

 **Greg Teasley**

**Springs/Flow:** As of today we still have good flow on both A and B lines.

I hiked up to the A source on 4/22 and found the catchment was full of gravel so I cleaned it out really well. I'm planning on making another trip across the river to check out the B source and to make a list of exactly what is needed to hook up to the other A source.

**Test Results:**

Water quality has been passing state standards.

**Water Plant:**

It has been working efficiently.

**Wastewater Plant:**

It is functioning properly and passing state tests. I removed all of the weeds from the north filtering bed and also a redwood tree that was growing right up against the chain link fence. There are still repairs that need to be addressed at the plant.

**Lift station:**

Still operating on only 1 pump, which seems to be keeping up with the load.

I met with an electrician and helped him remove part of the wire to the lift station. In doing so, I found that the wire was the reason that there was not enough voltage reaching the pump to operate it.

**Repairs & Leaks**

I repaired a leak on Newton road and replaced the meter box. I also dug out the Cal Fire meter box so that meter can be repaired or replaced in the future. There is a leak on Parish lane that I couldn't find until just recently thanks to Richard Amaral. Luckily, Parish lane isn't asphalt so it will be easier to dig up and repair.